|  |
| --- |
| **INSPECTION TEST AND PLAN EXAMPLE: A1, C2**  |
| **Contractor/customer:**  ABBC Engineering | **Date of issue: 1st July 2021** |
| **Project title:** Subiaco Treatment Plant  | **Prepared by: Joe Bloggs**  |
| **Water Corporation project No.:**  CW 1999999 | **Job/contract number: xxxxxxxxx** |
| **Description and system:**  Structural Steel and above ground piping  | **No. of pages: 3** |
|

|  |  |
| --- | --- |
| **Legend of inspection points:**

|  |
| --- |
|  **H = Hold Point.** Work may not proceed without approval or notification, unless approved by the principal or contractor.  **W = Witness Point.** Work may proceed without the presence of the principal. **S = Surveillance.** Witness at random, no formal notification required.  **V = Verify.** **R/A = Review.** Documents & Accept.**(work can proceed if principa**l **cannot attend hold point inspection within three hours of notified time for attendance)** |

 |

 |

| **No** | **Activity/Operation** | **Specification / Document**  | **Acceptable Criteria** | **Verifying Document**  | **Person Responsible** | **Inspection & Verification Points** |
| --- | --- | --- | --- | --- | --- | --- |
| **Sub-****Contractor** | **Sign** | **Contractor** | **Sign** | **Principal or Nominee** | **Sign** |
| 1 | Review client specifications | * Water Corporation DS95
* Specification A1
* Specification C2
 | Read and fully understand the requirements & responsibilities.  | Signed and approved ITP | QC Inspector | **R/A** |  | **R/A** |  | **V** |  |
| 2 | Blasting and coating applicators qualification | * Water Corporation DS95
* ASTM D4228
 | As per coating contractor’s internal procedure and standards. | Verification of competency record (VOC) | QC Inspector | **H** |  | **V** |  | **V** |  |
| 3 | Certificate of inspection personnel | * Water Corporation DS95
* NACE/ACA
 | Certified as per specification requirements. | NACE/ACA | QC Inspector | **V** |  | **V** |  | **W** |  |
| 4 | Calibration of all test equipment | * Water Corporation DS 95
* SSPC PA2
* AS3894.3
* ISO 17025
 | Equipment manufacturers criteria, qualified person, or NATA registered or equivalent testing facility. | Calibration and testing certificates and records. | QC Inspector | **H** |  | **W** |  | **W** |  |
| 5 | Substrate inspection  | * Water Corporation DS 95
* Specification A1
 | Surfaces checked for no sharp edges, have a 2mm radius, and weld spatter burrs, etc. are removed. | Daily coating and inspection report | Supervisor/ QC Inspector | **H** |  | **W** |  | **W** |  |
| 6 | Compressed air supply and clean air inspection | * ASTM D 4285-83
 | Compressed air shall be free from water and oil and tested each day. | Daily coating and inspection report | Supervisor/ QC Inspector | **H** |  | **W** |  | **W** |  |
| 7 | Surface cleanliness | * SSPC SP1
* AS3894.6
* AS1627.1
 | Oil, grease, dirt, and other foreign matter shall be removed. | Daily Inspection report | Daily Inspection report | **V** |  | **S** |  | **W** |  |
| 8 | Verify abrasive blast and surface profile | * Water Corporation DS 95
* Specification A1.
* AS 1627.4
* AS 3894.5
* AS3894.12
 | Class 3 (white metal) finish.SSPC-SP 5, SA-3.Surface profile as per coating manufacturers recommendation, typically 40-75 µm. | Daily coating and inspection report | QC Inspector | **H** |  | **S** |  | **S** |  |
|  9 | Test for chlorides.Required for C4 or C5 site/plant/yard locations | * Water Corporation DS 95
* Specification A1.
* AS 3894.6
 | Ambient service < 5µg/cm². | Daily coating and inspection report | QC Inspector | **H** |  | **V** |  | **W** |  |
| 10 | Test for particulate surface contamination | * Water Corporation DS 95
* Specification A1.
* AS 3894.6
* ISO 8502-3
 | Determination of surface dust pressure sensitive tape method.Dust level shall not exceed rating 2. | Daily coating and inspection report | QC Inspector | **V** |  | **W** |  | **S** |  |
| 11 | Ambient Conditions | * Water Corporation DS 95
* Specification A1
* Specification C2
* AS 3894.7
* AS 3894.13
 | Ambient conditions shall be recorded at least 4 times per shift.Max relative humidity 85%.Min/Max substrate Temp 10°C - 55°C.Min Substrate Temp 3oC above dew point. | Daily coating and inspection report | QC Inspector  | **H** |  | **W** |  | **W** |  |
| 12 | Stripe coatingperformed for primer and intermediate coat | * Water Corporation DS 95
* Water Corporation C2
 | Ensure all welds, edges, crevices, seams, joints, and corners are brush stripe coated.  | Daily coating and inspection report | QC Inspector | **V** |  | **W** |  | **W** |  |
| 13 | Apply 1st primer coat**Insert the Coating Product Name** | * Water Corporation DS 95
* Water Corporation C2
 | Monitor DFT after application.80 µm DFT. | Daily coating and inspection report | QC Inspector | **V** |  | **W** |  | **W** |  |
| 14 | Apply 2nd intermediate coating**Insert the Coating Product Nam** | * Water Corporation DS 95
* Water Corporation C2
 | Monitor WFT regularly during application.150 µm DFT. | Daily coating and inspection report | QC Inspector | **V** |  | **W** |  | **W** |  |
| 15 | Apply finish coating**Insert the Coating Product Name/Colour** | * Water Corporation DS 95
* Water Corporation C2
 | 50 µm DFT.The Total DFT 280 µm. | Daily coating and inspection report | QC Inspector | **H** |  | **H** |  | **W** |  |
| 16 | Final coat inspection | * Water Corporation DS 95
* Specification C2
* AS3894.3
* AS3894.4
* SSPC PA2
 | Visual inspection for runs, sags and any inclusions etc.Coating is cured and final DFT recorded. All batch numbers are documented.  | Daily coating and inspection report | QC Inspector | **H** |  | **H** |  | **W** |  |
| 17 | Verifying acceptancedocumentation | * Water Corporation DS 95
* AS3894.12
 | Check that all inspection, test documentation and completion reports have been completed and signed. Submit documentation to Contractor/Principal.  | Completion Report.IRC and signed ITP. | QC InspectorContractorPrincipal | **H/R** |  | **RA** |  | **RA** |  |
| **COMMENTS AND NOTES:** |
| Consider environmental conditions in relation to coastal C4 C5 location of works.Water blasting to remove soluble salts prior to abrasive blast cleaning and between coats might be a consideration for adding an inspection line item into the ITP. |
| Contractor then client to sign ITP at completion of works and ITP close out. |

Insert signature box of individual client acceptance for ITP details here